Veolia – Gum Springs Hazardous Waste Incinerator

811 Hasley Rd Arkadelphia, AR 71923

# REQUEST FOR PROPOSAL (RFP) Rev01

## Bulk Waste Additional HVAC Scope & Fly Ash Building Additional Heaters

## 1. PROJECT INFORMATION

Project: Veolia Arkadelphia – New Hazardous Waste Incinerator Project
Location: Arkadelphia, Arkansas
Owner: Veolia North America

## 2. SCOPE OF WORK

The Contractor shall furnish all labor, materials, equipment, supervision, and incidentals required to complete the remaining HVAC and heater scope described herein, in accordance with the contract drawings, specifications, equipment cut sheets, equipment Schedule and manufacturer requirements.

## 3. BULK WASTE BUILDING – ADDITIONAL HVAC SCOPE

### 3.1 Equipment & Locations

| Item | Equipment Tag | Location | Drawing Number |
| --- | --- | --- | --- |
| 1 | FA-0302-301 | Regulated Waste Shredder Enclosure – 3rd Floor including the dampers | VGS-MEC-0300-PLN-3002 |
| 2 | FA-0302-302 | Regulated Waste Shredder Platform – 4th Floor including the dampers | VGS-MEC-0300-PLN-3003 |
| 3 | FA-0404-303 | Apron Conveyor Enclosure – 5th Floor, including the dampers | VGS-MEC-0300-PLN-3004 |
| 4 | L-0302-105 (Qty 2) | Repack Area – 1st Floor (Opening done) | VGS-MEC-0300-PLN-3301 |
| 5 | L-0302-106 | Regulated Waste Shredder Enclosure | VGS-MEC-0300-PLN-3002 |
| 6 | L-0302-107 | Regulated Waste Shredder Platform – 4th Floor | VGS-MEC-0300-PLN-3003 |
| 7 | L-0404-108 | Apron Conveyor Enclosure – 5th Floor | VGS-MEC-0300-PLN-3004 |
| 8 | L-0404-109 | Apron Conveyor Enclosure – 5th Floor | VGS-MEC-0300-PLN-3004 |
| 9 | L-0404-110 (Qty 2) | Storage Area – 5th Floor (Opening done) | Storage Area Level 5 |
| 10 | CBD2 (Qty 8) | Backdraft Dampers – 1st Floor (5 pit louvers, 3 repack louvers) | VGS-MEC-0300-PLN-3301 |

### 3.2 Work Requirements

Contractor shall:

- Furnish and install all fans and louvers per Drawing VGS-MEC-0300-PLN-3006.

- Provide complete systems including bird screens, ductwork, dampers, motors, vibration isolators, guards, supports, channel strut, hanger rods, and flashing.

- Furnish and install five (5) counterbalanced backdraft dampers (CBD2) for Bulk Waste pit existing louvers.

- The louvers in the repack area shall have counterbalanced backdraft dampers.

- Seal all louvers and fans watertight per manufacturer instructions.

- Lower the existing heating unit in the Bulk Waste Control Room to below ceiling level, including all required support modifications and reconnections.

- Coordinate installation with field conditions and verify all dimensions prior to installation.

- Provide a Ruskin CBD2, or equal, counterbalanced backdraft damper installed behind the louvers within the sheet metal plenum. Damper shall be sized to match the louver face area.

- Duct to be SS steel.

## 4. FLY ASH BUILDING – HEATER SCOPE

Contractor shall:

- Furnish and install five (5) unit heaters with the thermostats on the second floor per Drawing VGS-MEC-0704-PLN-3300, including mounting at elevations shown.

- Modify the elevation of two (2) existing first-floor heaters such that the base of each heater is 12 feet above the finished floor noted on drawing. These do not need to be relocated. Disregard.

- Provide all supports, connections, and accessories required for a complete and operational installation.

## 5. STEAM BUILDING – ELECTRICAL ROOM A/C PAN

Contractor shall:

- Furnish and install condensate drain pan (65" x 34" x 2") with 3/4" discharge under the A/C unit inside the electrical room to prevent any risk of the condensate drain to the battery.

- Provide 1-5/8" Unistrut support system.

- Product information or approved equal: https://www.grainger.com/product/3HAJ7?gucid=N%3AN%3AFPL%3AFree%3AGGL%3ACSM-1946%3Atew63h3%3A20501231&utm_source=chatgpt.com

- Install approximately 15 LF of 3/4" PVC drain piping routed from the pan to the exterior north wall and down to pavement.

## 6. SUBMITTALS

Contractor shall provide:

- Shop drawings and vendor details for HVAC equipment, heaters duct work, and any other ancillary components

- Product data for fans, louvers, dampers, heaters, and drain pan

- Installation details and support/anchoring methods

- Manufacturer installation instructions

## 7. QUALITY REQUIREMENTS

- All work shall comply with project specifications and applicable codes.

- Installation shall follow manufacturer recommendations.

- Field verification of all dimensions is required.

## 8. PRICING FORMAT

| Description | Labor ($) | Material ($) | Subcontract ($) | Equipment ($) | Subtotal ($) |
| --- | --- | --- | --- | --- | --- |

## 9. CLARIFICATIONS

- Contractor shall include all incidental materials required for a complete system.

- All supports, fasteners, and installation hardware shall be included.

- Contractor is responsible for field measurements and coordination with other trades.

- Contractor shall include wall openings with the flashing and framing for the Apron conveyor enclosure HVAC and for the Regulated Waste Shredder enclosure and platform. The opening for the storage area and repack area are existing.

- All wall/roof penetrations shall be sealed and flashed watertight.

- Existing equipment modification includes disconnection, relocation, and reinstallation.

- Electrical power and controls are by others unless specifically noted.

## 10. EXCLUSIONS

Unless specifically included, the following are excluded:

- Major electrical work (power supply, MCC, controls integration)

- Fireproofing and insulation (unless noted)

- Painting except specified systems

- Crane/rigging beyond standard installation means

- Natural gas tie-in or piping.

## 11. SCHEDULE

Contractor shall provide:

- Project schedule with milestones

- Equipment lead times

## 12. GENERAL CONDITIONS

- Contractor shall comply with OSHA and site safety requirements.

- Coordinate all work with plant operations.